## 工作表1
Clause Number | Subject | Requirement of GS | Key Parameters | Type of Prove | Referenced Standard | EL-LT-01 | EL-LT-05 | EL-LT-07 | EL-LT-09 | EL-LT-12
7.2.9.1.1 | General – LED Luminaire & Driver | The 'Light Emitting Diode' (LED) luminaires, including the electronic driver and LED module shall be suitable for operation at 220 V ± 6%, 50 Hz ± 2%, single phase AC supply. | Voltage: 220 V ± 6%, Frequency: 50 Hz ± 2%, Single phase AC | Value | — | Compliance List P5 Certificate of Conformity P21 Test Report P28,32,68,87,91 | Compliance List P5 Certificate of Conformity P20 Test Report P28,32,68,89,93 | Compliance List P5 Certificate of Conformity 30 Test Report P52,87,88 | Compliance List P5 Certificate of Conformity P22 Test Report P19,40,80,81,136 | Compliance List P5 Certificate of Conformity P22 Test Report P23,25,27,30,35,36
7.2.9.1.2 | Factory Testing of LED Luminaire | The LED luminaires shall be fully assembled and tested before shipment from factory. Shall comply with relevant quality standard of ISO 9001:2015. | Full assembly, Pre-shipment testing, Quality management | Certficate | ISO 9001:2015 | Certificated for Luminaires P20 | Certificated for Luminaires P25 | Certificated for Luminaires P29 | Certificated for Luminaires P21 | Certificated for Luminaires P21
7.2.9.1.2 | Compliance with IEC 60598 Series | The LED luminaires shall comply with the following international standards and their manufacturing process shall conform to ISO 9001:2015: | — | Certficate | IEC 60598-1:2014+AMD1:2017 CSV – Part 1: General requirements and tests | Compliance List P5 Catalogue P18 Certificate of Conformity P21 Test Report P23,25,27,29,59,77 IEC 60598-1 IEC 60598-2-1 IEC 60598-2-22 | Compliance List P5 Catalogue P18 Certificate of Conformity P20 Test Report P27,29,34,56,59 IEC 60598-1 IEC 60598-2-1 IEC 60598-2-22 | Compliance List P5 Catalogue P18 Certificate of Conformity P30 Test Report P48,50,80,95,98,102,103,104 IEC 60598-1 IEC 60598-2-2-2 | Compliance List P5 Catalogue P18 Certificate of Conformity P22 Test Report P39,41,45,46,72,80,82,90,92,93,94 IEC 60598-1 IEC 60598-2-1 IEC 60598-2-22 | Compliance List P4 (not comply)
|  | IEC 60598-1:2014+AMD1:2017 CSV – Part 1: General requirements and tests |  |  | IEC 60598-2-1:1979/AMD1:1987 – Part 2: Fixed general purpose luminaires
|  | IEC 60598-2-1:1979/AMD1:1987 – Part 2: Fixed general purpose luminaires |  |  | IEC 60598-2-2:2011 – Part 2: Recessed luminaires
|  | IEC 60598-2-2:2011 – Part 2: Recessed luminaires |  |  | IEC 60598-2-3:2002+AMD1:2011 – Part 2: Luminaires for road and street lighting
|  | IEC 60598-2-3:2002+AMD1:2011 – Part 2: Luminaires for road and street lighting |  |  | IEC 60598-2-5:2015 – Part 2: Floodlights
|  | IEC 60598-2-5:2015 – Part 2: Floodlights |  |  | IEC 60598-2-13:2006+AMD1:2011+AMD2:2016 – Part 2: Ground recessed luminaires
|  | IEC 60598-2-13:2006+AMD1:2011+AMD2:2016 – Part 2: Ground recessed luminaires |  |  | IEC 60598-2-22:2014/AMD1:2017 CSV – Part 22: Emergency lighting
IEC 60598-2-22:2014/AMD1:2017 CSV – Part 22: Emergency lighting
7.2.9.1.2 | Type Test Certificate | Type test certificate shall be provided to demonstrate the compliance with the above standards issued by organisations accredited by HOKLAS or HKAS, or organisations accredited by an accreditation scheme mutually recognised by HOKLAS or HKAS for the LED luminaries. | Type test certificate by organisations with HOKLAS/HKAS accreditation | Details on the Certificate | HOKLAS / HKAS | Compliance List P5,7,9 Certificated for Luminaires P20 香港實驗所認可計劃相互承認安排伙伴-CNSA | Compliance List P5,7,9 Certificated for Luminaires P25 香港實驗所認可計劃相互承認安排伙伴-CNSA | Compliance List P5,7,9 Certificated for Luminaires P29 香港實驗所認可計劃相互承認安排伙伴-CNSA | Compliance List P5,7,9 Certificated for Luminaires P21 香港實驗所認可計劃相互承認安排伙伴-CNSA | Compliance List P4,6,8 Certificated for Luminaires P21 香港實驗所認可計劃相互承認安排伙伴-CNSA
7.2.9.1.3 | Compliance with Specific IEC Standards | The LED luminaires shall be marked in accordance with requirements of IEC 60598-2-1:1979/AMD1:1987 for general-purpose lumin+B13:C14aires or IEC 60598-2-2:2011 for recessed luminaires. Ingress protection for indoor, outdoor, underwater LED luminaires shall be at least IP2X, IP54, IP68 respectively to IEC 60529:1989/AMD2:2013/COR1:2019 . | Marking, IP ratings: Indoor ≥ IP2X, Outdoor ≥ IP54, Underwater ≥ IP68 | Value | IEC 60598-2-1:1979/AMD1:1987, IEC 60598-2-2:2011, IEC 60529:1989/AMD2:2013 COR1:2019 | Certificate of Conformity P21 Test Report P23,28,34,53,56,77,78 | Certificate of Conformity P20 Test Report P22,28,32,56,77 | Certificate of Conformity P30 Test Report P32,49,52,54,76,102 | Certificate of Conformity P22 Test Report P24,40,46,65,68,92,93 | Compliance List P4,5 (not comply)
7.2.9.1.4 | Radiance and Radiation Limits | The irradiance and radiance emission limits of the LED luminaires, that are exposed to view directly, shall be tested to comply with the hazard ‘Risk Group 1’ (low risk) unlimited as stated in the requirements of the IEC 62471:2006 and IEC/TR 62778:2014. | Risk Group 1 (viewing directly) | Value | IEC 62471:2006, IEC/TR 62778:2014 | Compliance List P6 Test Report P86,87,91,94 | Compliance List P6 Test Report P88,89,93,96 | Compliance List P6 Test Report P39,50,54,62,100,102 | Compliance List P6 Certificate of Conformity P26 Test Report P32,41,54,82,103,120 | Compliance List P5 Certificate of Conformity P26 Test Report P22,23,27,42
7.2.9.1.5 | Continuous Operation at High Temperature | The LED luminaires shall be rated for continuous service at an ambient temperature of 40°C without affecting the performance requirements as stated in Clause 7.2.9.4 of this General Specification. The Supervising Officer shall be advised if the performance of the LED luminaires will be affected by the installation conditions. | Ambient temp: 40°C, Continuous operation | Value | — | Compliance List P6,7 Test Report 67,68 | Compliance List P6,7 Test Report 67,68 | Compliance List P6,7 Test Report 86,87 | Compliance List P6,7 Test Report 79,81 | Compliance List P5,6
7.2.9.1.6 | RoHS Compliance | The LED luminaires components (circuit boards, electrical, electronic and plastic) shall comply with RoHS. | RoHS compliance | Written | — | Compliance List P6 | Compliance List P6 | Compliance List P6 Test Report P43 | Compliance List P6 Test Report P36 | Compliance List P5
7.2.9.1.7 | Photometric Data | The LED luminaires shall have a full set of photometric data prepared to CIBSE TM5 or IES format for general lighting purpose. | Photometric file format | Graph | CIBSE TM5, IES format | Photometric data P96-115 | Catalogue P18 | Catalogue P18 | Catalogue P18 | NIL
7.2.9.1.8 | Type of LED Luminaire | The type of LED Luminaires shall comply where applicable with the requirements as stipulated Clauses 7.2.7.2 to 7.2.7.5 of this General Specification. | Cross-reference to 7.2.7.2–7.2.7.5 | - | GSIBS-2022, Clauses 7.2.7.2–7.2.7.5 | Compliance List P6 | Compliance List P6 | Compliance List P6 | Compliance List P6 | Compliance List P5 (not comply)
7.2.9.2.1 | Electronic Driver | The electronic driver (driver) for the LED luminaire shall include the components of power factor correction, radio interference suppression and also dimming facility if it is specified. The driver shall conform to the following international standards if applicable: - | — | Certficate | BS EN IEC 55015:2019 | Compliance List P6 Test Report P45,46,56,59,68,91 IEC 61347 | Compliance List P6 Test Report P45,46,56,59,68,93 IEC 61347 | Compliance List P6 Test Report P40,65,79,87,88,118,124 IEC 61347 IEC 62384 | Compliance List P6,7 Catalogue P19 Test Report P133,135 IEC 55015 IEC 61000-3-2 IEC 61000-3-3 IEC 61347-1 IEC 61347-2 IEC 61547 IEC 62384 | Compliance List P5 Catalogue P19 Test Report P27,35 IEC 55015 IEC 61000-3-2 IEC 61000-3-3 IEC 61347-1 IEC 61347-2 IEC 61547 IEC 62384
|  | BS EN IEC 55015:2019 – Limits and methods of measurement of radio disturbance characteristics of electrical lighting and similar equipment. |  |  | BS EN IEC 61000-3-2:2018 – Part 3-2
|  | BS EN IEC 61000-3-2:2018 – Electromagnetic compatibility (EMC) – Part 3-2: Limits – Limits for harmonic current emissions (equipment input current <= 16 A per phase) |  |  | BS EN IEC 61000-3-3:2013 – Part 3-3
|  | BS EN IEC 61000-3-3:2013 – Electromagnetic Compatibility (EMC) – Part 3-3: Limits – Limitation of voltage changes, voltage fluctuations and flicker in public low-voltage supply systems, for equipment with rated current <=16A per phase and not subject to conditional connection |  |  | BS EN IEC 61347-1:2015+AMD1:2017 – Lamp controlgear – Part 1: General and safety requirements
|  | BS EN IEC 61347-1:2015+AMD1:2017 – Lamp controlgear – Part 1: General and safety requirements |  |  | BS EN IEC 61347-2-13:2014+AMD1:2016 – Lamp controlgear – Part 2-13
|  | BS EN IEC 61347-2-13:2014+AMD1:2016 – Lamp controlgear – Part 2-13: Particular requirements for D.C. or A.C. supplied electronic controlgear for LED modules |  |  | BS EN IEC 61547:2009 /ISH1:2013
|  | BS EN IEC 61547:2009 /ISH1:2013 – Equipment for general lighting purposes – EMC immunity requirements |  |  | BS EN IEC 62384:2006+AMD1:2009 CSV
BS EN IEC 62384:2006+AMD1:2009 CSV – D.C. or A.C. supplied electronic control gear for LED modules – Performance requirements
7.2.9.2.2 | Driver Performance Data | Technical information of the drivers shall be provided to indicate the performance of the drivers. The data shall include, but not limited to, minimum and maximum input voltage, frequency, maximum operating temperature, rated output voltage, rated output current, rated output power, power factor and radio interference suppression. | Full electrical performance data sheet, including rated output voltage, rated output current, rated output power, power factor, radio interference suppression, minimum and maximum input voltage, frequency, maximum operating temperature, rated output voltage ripple, output current ripple, power factor and radio interference suppression. | Value | — | Test Report P39,68,70 | Test Report P39,68,70 | Test Report P87,88 | Test Report P80,81 | NIL
7.2.9.2.3 | Driver Rated Life | The rated life of driver shall not be less than 35,000 hours operating at ambient temperature not lower than 40°C. | Driver’s lifetime >= 35,000 hrs @ >= 40°C | Value | — | Compliance List P7 Test Report P68 NO lifetime | Compliance List P7 Test Report P68 NO lifetime | Compliance List P7 Catalogue P18 | Compliance List P7 Test Report P19,80 | NIL
7.2.9.2.4 | Dimming Compatibility | Electronic ballast shall be compatible with dimming circuit provided. Unless otherwise specified, electronic ballast shall have at least continuous dimming range 40% – 100% without flickering. | Electronic ballast's Dimming range: 40% – 100%, No flicker | Value | — | Compliance List P7 (Not Comply) | Compliance List P7 (Not Comply) | Compliance List P7 (Not Comply) | Compliance List P7 (Not Comply) | Compliance List P6 (Not Comply)
7.2.9.3.1 | LED Module & Self-ballasted LED Lamp | LED module, self-ballasted LED module or self-ballasted LED lamp shall be manufactured and tested to comply with the following standards if applicable: | — | Certficate | IEC 62031:2018 – LED modules for general lighting – Safety specifications | Compliance List P7 IEC 60838-2-2 (Not Comply) | Compliance List P7 IEC 60838-2-2 (Not Comply) | Compliance List P7 Certificate of Conformity P30,34 IEC 60838-2-2 (Not Comply) | Compliance List P7 Certificate of Conformity P22,26 IEC 60838-2-2 (Not Comply) | Compliance List P6 Certificate of Conformity P38,39,42 IEC 60838-2-2 (Not Comply)
|  | IEC 62031:2018 – LED modules for general lighting – Safety specifications |  |  | IEC 62717:2014+AMD1:2015+AMD2:2019 – LED modules for general lighting – Performance requirements
|  | IEC 62717:2014+AMD1:2015+AMD2:2019 – LED modules for general lighting – Performance requirements |  |  | IEC 60838-2-2:2006+AMD1:2012 – Miscellaneous lampholders – Part 2-2: Connectors for LED modules
IEC 60838-2-2:2006+AMD1:2012 – Miscellaneous lampholders – Part 2-2: Connectors for LED modules
7.2.9.3.1 | LED Module Certificate | Certificate of compliance with the above standards shall be issued by organisations accredited by HOKLAS or HKAS, or organisations accredited by an accreditation scheme mutually recognised by HOKLAS or HKAS or the manufacturer of LED module. | Type test certificate by organisations, with HOKLAS/HKAS recognition or organisations accredited by an accreditation scheme mutually recognised by the manufacturer of LED module. | Certficate | HOKLAS / HKAS | Certificate P20,122,123 香港實驗所認可計劃相互承認安排伙伴-CNSA | Certificate P25,103-106 香港實驗所認可計劃相互承認安排伙伴-CNSA | Certificate P29,36,47,117 香港實驗所認可計劃相互承認安排伙伴-CNSA 香港實驗所認 | Certificate P21,29,35,138 香港實驗所認可計劃相互承認安排伙伴-CNSA | Certificate P21,34 香港實驗所認可計劃相互承認安排伙伴-CNSA
7.2.9.4.1 | Performance Requirements – General | Each type of LED module, LED luminaire or self-ballasted LED lamp shall be fully assembled with all the associated components. The performance of the LED module, LED luminaire and self-ballasted LED lamp shall comply with the following requirements: | Full assembly, Performance compliance | Value | — | NIL | NIL | NIL | NIL | NIL
7.2.9.4.1 (a) | Luminaire Efficacy | The luminaire efficacy of different types of luminaires under different colour temperatures to be used in the Contract shall be provided to indicate its performance. | Efficacy (lm/W) per CCT | Value | — | Test Report P96,106 | NIL | Catalogue P18 | Catalogue P18 | NIL
7.2.9.4.1 (b) | Lumen Maintenance (L₇₀) | The lumen maintenance of LED module shall not be less than 90% of its initial value until an operating time of 25% rated life or 6,000 hours. The lumen output of LED luminaire shall deliver at least 70% of its initial lumen output after operating 35,000 hours and 25,000 hours for LED luminaire and self-ballasted LED lamp respectively. For compliance with the L70 threshold lumen maintenance requirements, the lumen maintenance data of each colour temperature LED luminaire using 6,000 hours is acceptable for projecting the L70. The required lumen maintenance at 6,000 hours shall not be less than 94.1% and 91.8% for L70 = 35,000 hours and L70 = 25,000 hours respectively. | L₉₀ >= 90% until 25% rated life or 6,000 hours (LED module), L₇₀ >= 70% @ 35,000 hrs (LED luminaire), L₇₀ >= 70% @ 25,000 hrs (self-ballasted LED lamp), Projection allowed using 6,000 hr data (LED luminaire), Lumen maintenance @ 6,000 hrs: L₇₀ >= 94.1% (35,000 hrs), L₇₀ >= 91.8% (25,000 hrs) | Value | — | Compliance List P8 | Compliance List P8 | Compliance List P8 | Compliance List P8 | Compliance List P7
7.2.9.4.1 (c) | Colour Rendering Index (CRI) | CRI shall be minimum 80 for colour temperature from 2,700 – 6,000 K for indoor luminaires and self-ballasted LED lamp. | CRI ≥ 80, CCT: 2,700–6,000 K | Value | — | Compliance List P8 Test Report P96,106 | Compliance List P8 Test Report P59 | Compliance List P8 Catalogue P18 Test Report P51,107 | Compliance List P8 Catalogue P18 Test Report P123 | Compliance List P7 Catalogue P18 Test Report P25,30,36
7.2.9.4.1 (d) | Power Factor | The power factor of the LED luminaire circuit and self-ballasted LED lamp shall be minimum 0.9 and minimum 0.7 respectively. | PF ≥ 0.9 (luminaire), PF ≥ 0.7 (self-ballasted) | Value | — | Compliance List P8 Test Report P70 | Compliance List P8 Test Report P70 | Compliance List P8 Catalogue P18 Test Report P90 | Compliance List P8 Catalogue P19 Test Report P84,85 | Compliance List P7 Catalogue P18
7.2.9.4.1 (e) | Correlated Colour Temperature (CCT) & Tolerance | The colour temperature of a group of LED luminaires in the same space or room shall not be visually noticeable. The nominal CCT of the LED light source shall preferably be one of the following values. The tolerance limits shall be within the below ranges: - 2,700 K 2,725 ± 145 K 3,000 K 3,045 ± 175 K 3,500 K 3,465 ± 245 K 4,000 K 3,985 ± 275 K 4,500 K 4,503 ± 243 K 5,000 K 5,028 ± 283 K 5,700 K 5,665 ± 355 K 6,500 K 6,530 ± 510 K | Nominal CCT: 2,700K, 3,000K, 3,500K, 4,000K, 4,500K, 5,000K, 5,700K, 6,500K, Tolerance: ±145K, 175, 245, 275, 243, 283, 355 and 510K | Value |  | Compliance List P8 Test Report P89,94,96,106 | Compliance List P8 Test Report P91,96 | Compliance List P8 Test Report P51,107 | Compliance List P8 Test Report P123 | Compliance List P7 Catalogue P18 Test Report P25,30,36
7.2.9.4.2 | Testing by Accredited Laboratory | Each model of LED module, LED luminaire or self-ballasted LED lamp shall be tested to comply with the above performance requirements. The test report from the organisations accredited by HOKLAS or HKAS, or organisations accredited by an accreditation scheme mutually recognised by HOKLAS or HKAS shall be submitted to certify each model of LED module, LED luminaire or self-ballasted LED lamp complying with the standards or other recognised international/national standards or other standards proposed and agreed by the Supervising Officer. | Test report by organizations with HOKLAS/HKAS accreditation | Test report | HOKLAS / HKAS | Certificated for Luminaires P20 | Certificated for Luminaires P25 | Certificate for Luminaires P29 | Certificate for Luminaires P21 | Certificate for Luminaires P21
7.2.9.4.3 | Self-ballasted LED Lamps – Additional Standards | Self-ballasted LED lamps for general lighting services shall comply with: | — | Certficate | IEC 62560:2011/COR2:2015 - Self-ballasted LED lamps for general lighting services by voltage > 50V – Safety specifications | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply)
|  | IEC 62560:2011/COR2:2015 - Self-ballasted LED lamps for general lighting services by voltage > 50V – Safety specifications |  |  | IEC 62612:2013+AMD1:2015+AMD2:2018 – Self-ballasted LED lamps for general lighting services with supply voltages > 50 V - Performance Requirements
IEC 62612:2013+AMD1:2015+AMD2:2018 – Self-ballasted LED lamps for general lighting services with supply voltages > 50 V - Performance Requirements
7.2.9.4.4 | Double-capped LED Tubular Fluorescent Lamp | For double-capped LED tubular lamp intends to retrofit tubular fluorescent lamp, the LED lamp shall comply with IEC62776:2014/ISH1:2018 “Double-capped LED Lamps Designed to Retrofit Linear Fluorescent Lamps – Safety Specifications”. Where LED tubular lamp with built-in sensors is specified, the LED lamp shall be integrated with motion sensors and/or daylight sensors. The sensors shall be capable to control the lumen output of LED lamp to maintain the setting illuminance in a given area. The sensors shall meet the relevant requirements of Clause 7.2.4.8. | Double-capped LED tubular lamps, built-in Sensors Requirement: LED tubular lamp must integrate motion sensors and/or daylight sensors. Functionality: Sensors must control lumen output to maintain set illuminance in a given area. Compliance Clause: Sensors shall meet relevant requirements of Clause 7.2.4.8. | Written | IEC 62776:2014/ISH1:2018, Clause 7.2.4.8 | Test Report P90,91,92,94 | Test Report P92 to 96 | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Test Report P26,27,28
7.2.9.4.5 | Energy Label under VELLES | Self-ballasted LED lamp up to 60W shall have obtained a Grade 1 Energy Label under the Voluntary Energy Efficiency Labelling Scheme of Electrical and Mechanical Services Department. | Grade 1 for LED lamp up to 60W comply with EMSD VELLES (Hong Kong) | Certficate | EMSD VELLES (Hong Kong) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P9 (Not Comply) | Compliance List P8 (Not Comply)
7.1.4.1 | Pendant (Tube pendant) | Tube pendant shall comprise a dome cover and a biscuit ring and a piece of screwed steel conduit of suitable length to give the required mounting height of the luminaire. | Pendant (Tube pendant): Dome cover, biscuit ring, screwed steel conduit, suitable length for required mounting height | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1 | Pendant (Plain pendant) | Plain pendant shall comprise a ceiling rose and a cord-grip lampholder connected by a flexible cord having a suitable length to give the required mounting height of the lamp shade. | Pendant (Plain pendant): Ceiling rose, cord-grip lampholder, flexible cord, suitable length for required mounting height | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.2 | Luminaire Mounted on Pattress | When a luminaire is not provided with facility for a surface cable entry, the luminaire shall be mounted on pattress. The cable shall then enter the luminaire from the rear through a slot and a hole formed in the pattress. | Luminaire Mounted on Pattress: Surface cable entry not provided when mount on pattress; cable entry from rear via slot and hole in pattress | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.3 | Ceiling Rose | Ceiling rose shall not be used for the attachment of more than one outgoing flexible cord or cable unless it is specially manufactured for multiple pendants. | Ceiling Rose: Not more than one outgoing flexible cord/cable; exception: specially manufactured for multiple pendants | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.4 | Painting (Lighting equipment and luminaires) | Unless otherwise specified, lighting equipment and luminaires other than those indicated to be self-finished (such as stainless steel, anodised aluminium, etc.) shall have factory-finished. | Painting (Lighting equipment and luminaires): Factory-finished; exception: self-finished materials (stainless steel, anodised aluminium, etc.) or otherwise specified | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.4 | Painting (Metal parts for adaptable boxes, blanking plate) | Metal parts such as cover plates for adaptable boxes, blanking plate for any boxes and surface conduit, etc. shall be painted white or a suitable colour to match the interior finish of a particular location. | Painting (Metal parts for adaptable boxes, blanking plate): Painted white or suitable matching colour | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Weather resistance) | Outdoor luminaires shall be able to withstand the weather. | Outdoor Luminaires: Withstand weather | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Corrosion protection) | Metal work shall be protected against corrosion, and parts which have to be removed for access to the interior shall be provided with proper gaskets to restrict the entrance of moisture and dirt. | Outdoor Luminaires: Corrosion protection; proper gaskets for removable parts | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Mounting brackets) | Mounting brackets shall be heavily galvanised and stainless steel or galvanised bolts and nuts shall be used. | Outdoor Luminaires: Heavily galvanised mounting brackets; stainless steel or galvanised bolts and nuts | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Adjustment bolts and nuts) | The adjustment bolts and nuts of a luminaire which is mounted on high level shall be captive to prevent accidental loss during servicing. | Outdoor Luminaires: Adjustment bolts and nuts captive to prevent accidental loss | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Safety chains) | Safety chains shall be provided to hold the luminaire from falling. | Outdoor Luminaires: Safety chains provided | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Luminaire installed in a location within hand reach) | A luminaire installed in a location within hand reach shall be of robust construct, fitted with an impact-resistant transparent or diffusing front panel, and shall have have secret key fixings for the panel to the body of the luminaire. Where necessary, wire guards shall be fitted over the front panel to give extra protection or vandal proof luminaire shall be used. | Outdoor Luminaires within hand reach: Robust construct; impact-resistant transparent or diffusing front panel; secret key fixings; wire guards or vandal proof (optional) | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Cables within outdoor luminaire) | Cables within the outdoor luminaire shall be such a type that it can sustain the lamp operation at a high ambient temperature due to the waterproof/airtight natures of the luminaire. Heat resistant cable is considered as an acceptable mean of internal cable for outdoor luminaire. | Outdoor Luminaires: Cables sustain high ambient temperature; heat resistant cable acceptable | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Cable type certification) | Any other cable type with appropriate type test certification demonstrating satisfactory use for outdoor luminaire shall be submitted for approval by the Supervising Officer. | Outdoor Luminaires: Cables comply type test certification; approval by Supervising Officer | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Heat resistant sleeve) | Heat resistant sleeve shall be used for external cable entering the luminaire for wiring connection as far as practicable. Where installation of heat resistant sleeve is found impracticable due to environmental constraints, alternative mean avoiding cause of adverse effect as a result of high internal operating temperature shall be submitted for Supervising Officer's approval. | Outdoor Luminaires: Cables comply heat resistant sleeve for external cable; alternative mean subject to approval | Written | — | NIL | NIL | NIL | NIL | NIL
7.1.4.1.5 | Special Requirements for Outdoor Luminaires (Heat resistant sleeve extended) | Where the heat resistant sleeves is required, the sleeves within the luminaire shall be extended to a distance of 150 mm outside the luminaire. | Outdoor Luminaires: Cables comply heat resistant sleeve extends to 150 mm outside the luminaire | Written | — | NIL | NIL | NIL | NIL | NIL

## LAB
香港實驗所認可計劃(HOKLAS) - 相互承認安排(MRA)
https://www.itc.gov.hk/ch/quality/hkas/information/mra_mla_arrangements.html
香港實驗所認可計劃相互承認安排伙伴